## Slide 1: Corrosion Control
Using orthophosphate as primary corrosion inhibitor to prevent lead in drinking water

## Slide 2: Agenda
Health effects of lead
Lead in drinking water
Corrosion control treatment

## Slide 3: Health effects of lead
Children – behavior and learning problems, low IQ, and slowed growth
Pregnant Women – reduced fetus growth and premature birth
Adults – cardiovascular problems and reproducibility issues

## Slide 4: Lead in drinking water
Source - Home plumbing (Lead service lines and lead solder)
Mechanism – Non-passivated lead (Pb2+) reacts with water to form PbO. This compound is highly soluble and leaches into the drinking water.
Regulations – The Lead and Copper Rule (LCR) mandates that a system must demonstrate Optimized Corrosion Control Treatment (OCCT) by sampling at customers tap for lead and copper.
  Action Level – 90th percentile of samples must be less than 0.015 mg/L or 15 𝜇g/L

## Slide 5: Corrosion Control Treatment
Orthophosphate – utilities add orthophosphate (PO4) to react with the lead pipe material to form insoluble compounds that act as a barrier from the lead reaching the bulk water – this is called scale
Compounds – This forms hydroxypryomorphite and chloropyromorphite, which are both highly insoluble in water

## Slide 6: Conclusion
Lead in drinking water is a serious issue with a direct connection to public health
Lead enters the drinking water via lead pipes or solder in the home plumbing
Lead can be prevented from reaching the bulk water with the formation of insoluble compounds, that form scale on the pipe wall, when orthophosphate reacts with the lead material.